	Reference Number:

EMS-WI-AE004
	FORT RUCKER

Environmental Management System
	Revision Number:

001

	Title:
 Refrigerant Management Program

	Approved By:

Joseph A. Davis
	Issue Date:

14 April 2008


	Reference Number:

EMS-WI-AE004
	FORT RUCKER

Environmental Management System
	Revision Number:

001

	Title:
Refrigerant Management Program



Table of Contents

Section I. 

Purpose and Scope............................................................................................................2

Section II. Definitions........................................................................................................................3

Section III. Responsibilities................................................................................................................ 7

Section IV. 
Best Management Practices........................................................................................... 7-13

Section V. 
Recycling and Recovery Equipment...............................................................................14

Section VI. 
Technician Training/Certification.................................................................................. 14

Section VII. 
Recordkeeping................................................................................................................ 15

ATTACHMENT A: 
Field Sheet..............................................................................................................…….16

ATTACHMENT B: 
General ODC Turn-in Procedure……………………..................................................17-20

ATTACHMENT C: 
Contractor Agreement .................................................................................................... 21

Section I. Purpose and Scope

The purpose of the Fort Rucker Refrigerant Management Program (RMP) is to:

· Maximize the recycling of ozone depleting chemicals (ODC) and to minimize the release of ODC to the ambient air from the servicing, repairing, maintaining, and disposing of refrigeration appliances;

· Utilize certified technicians for the servicing, repairing, maintaining, and disposing of refrigeration appliances;

· Maintain proper records of refrigerant consumption, technician training, and recycling and recovery equipment certification;

· Ensure proper repairs are made for units with significant leak rates; and

· To ensure Fort Rucker is in full compliance with Section 608 of the Clean Air Act Amendments and the requirements of 40 CFR Part 82, Subpart F.

To achieve the objectives stated above Fort Rucker requires all personnel whose job duties require the handling, ordering, repairing, servicing, maintaining, or disposing of refrigerant or refrigeration appliances to review and comply with this written program.

Section II. Definitions

For the purposes of Fort Rucker’s RMP, the following definitions, as excerpted from 40 CFR Part 82.152, apply:
Appliance- any device which contains and uses a Class I or Class II substance as a refrigerant, including any air conditioner, refrigerator, chiller, or freezer.

Low-pressure appliance- an appliance that uses a refrigerant with liquid phase saturation pressure below 45 psia at 104 °F. This definition includes but is not limited to appliances using R–11, R–123, and R–113.

Medium-pressure appliance- an appliance that uses a refrigerant with a liquid phase saturation pressure between 45 psia and 170 psia at 104 °F. This definition includes but is not limited to appliances using R–114, R– 124, R–12, R–401C, R–406A, and R–500.

High-pressure appliance- an appliance that uses a refrigerant with a liquid phase saturation pressure between 170 psia and 355 psia at 104 °F. This definition includes but is not limited to appliances using R–401A, R– 409A, R–401B, R–411A, R–22, R–411B, R–502, R–402B, R–408A, and R–402A.
Very high-pressure appliance- an appliance that uses a refrigerant with a critical temperature below 104 °F or with a liquid phase saturation pressure above 355 psia at 104 °F. This definition includes but is not limited to appliances using R–13 or R–503.

Certified refrigerant recovery or recycling equipment- equipment certified by an approved equipment testing organization to meet the standards in 40 CFR Part 82.158 (b) or (d), equipment certified pursuant to 40 CFR Part 82.36 (a), or equipment manufactured before November 15, 1993, that meets the standards in 40 CFR Part 82.158 (c), (e), or (g).
Disposal- The process leading to and including:

(1) The discharge, deposit, dumping or placing of any discarded appliance into or on any     

      land or water;

(2) The disassembly of any appliance for discharge, deposit, dumping or placing of its

     discarded component parts into or on any land or water; or

(3) The disassembly of any appliance for reuse of its component parts.
Fort Rucker Personnel- military, civilian, tenants at the installation, contractors and subcontractors performing refrigeration maintenance on Fort Rucker property.
Full charge- the amount of refrigerant required for normal operating characteristics and conditions of the appliance as determined by using one of the following four methods or a combination of one of the following four methods:

(1) The equipment manufacturers’ determination of the correct full charge for the 

      equipment;

(2) Determining the full charge by appropriate calculations based on component sizes, 

      density of refrigerant, volume of piping, and all other relevant considerations;

(3) The use of actual measurements of the amount of refrigerant added or evacuated from 

      the appliance; and/or

(4) The use of an established range based on the best available data, regarding the normal

      operating characteristics and conditions for the appliance, where the mid-point of the

      range will serve as the full charge, and where records are maintained in accordance   

      with 40 CFR Part 82.166 (q). 
Initial verification test - leak tests that are conducted as soon as practicable after a repair is completed. An initial verification test, with regard to the leak repairs that require the evacuation of the appliance or portion of the appliance, means a test conducted prior to the replacement of the full refrigerant charge and before the appliance or portion of the appliance has reached operation at normal operating characteristics and conditions of temperature and pressure. An initial verification test with regard to repairs conducted without the evacuation of the refrigerant charge means a test conducted as soon as practicable after the conclusion of the repair work.

Low-loss fitting- any device that is intended to establish a connection between hoses, appliances, or recovery or recycling machines and that is designed to close automatically or to be closed manually when disconnected, minimizing the release of refrigerant from hoses, appliances, and recovery or recycling machines.

Major maintenance, service, or repair- any maintenance, service, or repair involving the removal of any or all of the following appliance components: compressor, condenser, evaporator, or auxiliary heat exchanger coil.

Motor vehicle air conditioner (MVAC)- any appliance that is a motor vehicle air conditioner as defined in 40 CFR Part 82, Subpart B (i.e. mechanical vapor compression refrigeration equipment used to cool the driver’s or passenger’s compartment of any motor vehicle. This definition is not intended to encompass the hermetically sealed refrigeration systems used on motor vehicles for refrigerated cargo and the air conditioning systems on passenger buses using HCFC–22 refrigerant).

MVAC-like appliance- mechanical vapor compression, open-drive compressor appliances used to cool the occupant’s compartment of an non-road motor vehicle. This includes the air-conditioning equipment found on agricultural or construction vehicles.

Opening an appliance- any service, maintenance, repair, or disposal of an appliance that would release refrigerant from the appliance to the atmosphere unless the refrigerant was recovered previously from the appliance. Connecting and disconnecting hoses and gauges to and from the appliance to measure pressures within the appliance and to add refrigerant to or recover refrigerant from the appliance shall not be considered ‘‘opening.’’
Ozone Depleting Chemicals (ODC) and Ozone Depleting Substances (ODS)- These terms are used interchangeably. A list of Class I ODCs is provided in the Army ODC Elimination Plan.
Reclaim refrigerant- to reprocess refrigerant to at least the purity specified in appendix A to 40 CFR Part 82, Subpart F (based on ARI Standard 700–1993, Specifications for Fluorocarbon and Other Refrigerants) and to verify this purity using the analytical methodology prescribed in appendix A. In general, reclamation involves the use of processes or procedures available only at a reprocessing or manufacturing facility.

Refrigerant- any substance consisting in part or whole of a class I or class II ozone-depleting substance that is used for heat transfer purposes and provides a cooling effect, or any substance used as a substitute for such a class I or class II substance by any user in a given end-use, except for the following substitutes in the following end-uses: 

(1) Ammonia in commercial or industrial process refrigeration or in absorption units; 

(2) Hydrocarbons in industrial process refrigeration (processing of hydrocarbons); 

(3) Chlorine in industrial process refrigeration (processing of chlorine and chlorine compounds); 

(4) Carbon dioxide in any application; 

(5) Nitrogen in any application; or 

(6) Water in any application.

Ozone Depleting Chemical Compliance Manager (ODCCM)-  a Facility, HVAC or other Manager that accurately tracks appliance information including refrigerant usage, leaks, disposal, and service records.

Self-contained recovery equipment- refrigerant recovery or recycling equipment that is capable of removing the refrigerant from an appliance without the assistance of components contained in the appliance.

Small appliance- any of the following products that are fully manufactured, charged, and

hermetically sealed in a factory with five (5) pounds or less of refrigerant: refrigerators and freezers designed for home use, room air conditioners (including window air conditioners and packaged terminal air conditioners), packaged terminal heat pumps, dehumidifiers, under-the-counter ice makers, vending machines, and drinking water coolers.

Substitute- any chemical or product, whether existing or new, that is used by any person as an EPA approved replacement for a class I or II ozone-depleting substance in a given refrigeration or air conditioning end-use.

Technician- any person who performs maintenance, service, or repair, that could be reasonably expected to release refrigerants from appliances, into the atmosphere. Technician also means any person who performs disposal of appliances, except for small appliances, MVACs, and MVAC-like appliances, which could be reasonably expected to release refrigerants from the appliances into the atmosphere. Performing maintenance, service, repair, or disposal could be reasonably expected to release refrigerants only if the activity is reasonably expected to violate the integrity of the refrigerant circuit. Activities reasonably expected to violate the integrity of the refrigerant circuit include activities such as attaching and detaching hoses and gauges to and from the appliance to add or remove refrigerant or to measure pressure and adding refrigerant to and removing refrigerant from the appliance. Activities such as painting the appliance, rewiring an external electrical circuit, replacing insulation on a length of pipe, or tightening nuts and bolts on the appliance are not reasonably expected to violate the integrity of the refrigerant circuit. Performing maintenance, service, repair, or disposal of appliances that have been evacuated pursuant to 40 CFR Part 82.156 could not be reasonably expected to release refrigerants from the appliance unless the maintenance, service, or repair consists of adding refrigerant to the appliance. Technician includes but is not limited to installers, contractor employees, in-house service personnel, and in some cases owners and/or operators.

Section III. Responsibilities

Refrigerant Technician

The Refrigerant Technician will be responsible for compliance with Section 608 and 609 of the Clean Air Act Amendments, the requirements of 40 CFR Part 82, Subpart F, and the Fort Rucker Refrigerant Management Program. The Refrigerant Technician will comply specifically with the following:

· Complete required records for all refrigerant related activities;

· Ensure recovery units meet evacuation requirements as detailed in EPA     

      regulations;

· Follow procedures to eliminate refrigerant contamination and mixing;

· Perform proper refrigerant recovery procedures as required;

· Perform initial leak tests using an acceptable method prior to charging refrigerant into a system;

· Perform annual leak audits on all equipment with greater than 50 pounds of refrigerant;
· Notify the Directorate of Public Works Environmental and Natural Resources Division (DPW ENRD) if a member of personnel is observed violating regulatory requirements.

Ozone Depleting Chemical Compliance Manager (ODCCM)

The ODC Compliance Manager will have responsibility for following the Fort Rucker RMP, specifically the following:

· Ensure all technicians in their department follow the requirements of the RMP;
· Report any violations of the RMP by personnel DPW ENRD;

· Maintain refrigerant recovery equipment certification;

· Provide the equipment owner a record and/or invoice that indicates the amount of refrigerant added to all appliances;

· Bi-annually maintain, check, leak test and document recovery unit maintenance pursuant to manufacturer's recommendations;
· Ensure entry of all data from refrigerant work done on post is entered in a timely manner into a RMP database.
Air Quality Program Manager

The DPW ENRD Air Quality Program Manager shall delegate the responsibility of implementing the RMP including: 
· Auditing RMP annually;

· Reviewing regulatory updates for changes; and

· Ensuring proper reporting to the Environmental Protection Agency (EPA) and the Alabama Department of Environmental Management (ADEM) as required. 

Section IV. Best Management Practices

To meet the objectives set forth in Section I of this RMP, Fort Rucker contractors and subcontractors shall comply with the following best management practices:

1) When any work is conducted on a refrigerant containing appliance, Fort Rucker personnel will   

     complete a field sheet (Attachment A) documenting all information pertaining to the work    

     completed, including but not limited to the appliance serviced, type and amount of refrigerant    

     collected/charged, results of leak tests, and date work was performed.

2) Prior to the disposal or recycling of any appliance owned and/or operated by Fort Rucker or 
    its tenants, except small appliances, motor vehicle air conditioners (MVAC), and MVAC-like 
    appliances, the unit and all associated piping shall be entirely evacuated to a certified recovery 
    or recycling machine. Fort Rucker personnel opening appliances for repair or servicing will    

    evacuate the entire unit or the part of the unit to be serviced to a certified recovery or recycling 
    machine. A certified technician must verify that the level of evacuation has been reached. All 
    appliances, except small appliances, motor vehicle air conditioners (MVAC), and MVAC-like  

    appliances, must be evacuated to the following level prior to opening the device.

TABLE 1

REQUIRED LEVELS OF EVACUATION FOR FORT RUCKER APPLIANCES

[Except for small appliances, MVACs, and MVAC-like appliances]

[image: image8.png]I Special Handling Procedures for Halon 1301 System Cylinders

A. Halon 1301 is typically incorporated into built-in fire suppression systems
applications with the charged Halon cylinder connected to the system piping. Because the Halon
is over pressurized with nitrogen to facilitate distribution, these system cylinders are usually
disconnected from the system and used as the transportation cylinder to return the product to the
Reserve as the systems are taken out of service. However, fire suppression system cylinders and
canisters with electrical charges or initiators must be deactivated prior to shipment to the
Defense Reserve. Special care should be taken when deactivating and disassembling the
systems. The valves on these cylinders are designed in a manner that upon activation, they are
changed instantly from a closed position to fully open position and will dispense the Halon in
less than 10 seconds. The combination of these sensitive valves and the high pressure within the
cylinders require compliance with good safety practices.

B. Instructions for dismantling a Halon Fire Suppression System are provided as
follows:

1. The first step is to deactivate the actuation system, which is usually electrical or
pneumatic. However, disconnection from the electrical or pneumatic source is not sufficient
from a safety standpoint. In the case of pneumatic systems, there is often still a small pin
exposed that must be covered with a safety cap before handling. Just the slightest touch on this
pin could cause full activation of the valve. In the case of electrically activated valves, simple
disconnection of the electrical leads to solenoid valves is acceptable. However, if the electrical
connection is to an explosive initiator, it is very important to remove the initiator. This is a very
important safety practice, because static electricity can cause the explosive to detonate. These
actions should be done before any other dismantling is initiated.

2. The next step is to disconnect any discharge piping from the discharge port.
Immediately upon disconnection of the piping, install an anti-recoil device (discharge port safety
cap). Safety caps should be used to cover exposed actuation mechanisms and discharge ports on
these special cylinders, otherwise dangerous safety situations could arise during the shipping,
receiving, or storage process. Application of manufacturer's designed and supplied caps are the
proper safety practice. In some cases the threads are not exactly the same as pipe threads and
may not hold under the pressure of release. However, if pipe caps, plugs or plates are substituted
for manufacturer's caps, at least four opposing holes must be drilled in the anti-recoil cap, plug or
plate to disperse any release of the Halon if the valve inadvertently activates. Anti-recoil device
safety caps/plugs/plates must always be in place before handling the cylinders.

3. Adherence with the above safety practices is paramount before removing any
cylinders from the mounting position. Once the safety devices are in place, cylinders can be
moved with relative safety. However, these are high-pressure compressed gas cylinders and
require all the safe handling practices of any other gas cylinder. Also, protective safety wear is
required for personnel deactivating cylinders.




3) Prior to disposal of appliances, Fort Rucker personnel shall evacuate to the levels included in 
    the table above, unless due to leaks in the appliance such levels are not attainable or would 
    significantly contaminate the refrigerant being recovered. In such cases, Fort Rucker  

    contractors/subcontractors will:

· Isolate leaking from non-leaking components when possible; 

· Evacuate non-leaking components to the levels listed in Section III, Table 1;

· Evacuate leaking components to the lowest level attainable without significantly

      contaminating the refrigerant being recovered (such level shall not exceed 0 psig).

4) Prior to opening small appliances, Fort Rucker personnel shall:

· Recover at least 80% of the refrigerant in the appliance when using recycling and recovery equipment manufactured before November 15, 1993; or

· Recover at least 90% of the refrigerant in the appliance when the compressor is operating or 80% of the refrigerant in the appliance when the compressor is not operating using recycling and recovery equipment manufactured on or after November 15, 1993; or

· Evacuate the small appliance to four inches of mercury vacuum.

5) Fort Rucker personnel will open MVAC-like appliances for service,  maintenance, or repair 
    only when properly operating certified recycling and recovery equipment.

6) All Fort Rucker personnel opening appliances including small appliances and MVACs for 
    maintenance, service, or repair will have a certified recycling and recovery device available.

7) Fort Rucker personnel will not use system dependent recovery equipment with appliances  

    containing a normal charge greater than fifteen pounds, unless such equipment is permanently 
    attached to the device as a pump out unit.

8) Fort Rucker personnel shall use all recycling and recovery equipment in accordance with 
    manufacturer’s directions, unless such directions do not comply with the requirements of 40  

    CFR Part 82.

9) Fort Rucker personnel may return refrigerant to the appliance it was removed from or to  

    another appliance under Fort Rucker’s ownership, without being recycled or reclaimed, unless   

    the device is a MVAC or MVAC-like device.

10) Fort Rucker personnel will not recycle any appliance in which the refrigerant has not been 
      recovered.

11) When recovering refrigerant from MVAC and MVAC-like devices for disposal, Fort Rucker  

      personnel will reduce system pressure to at or below 102 millimeters of mercury vacuum 
      using certified recycling and recovery equipment.

12) When recovering refrigerant from small appliances for purposes of disposal of the appliance, 
       Fort Rucker personnel will recover 90% of the refrigerant when the compressor is operating 
       or 80% of the refrigerant when the compressor is not operating or evacuate the small 
       appliance to four inches of mercury vacuum.

13) For any commercial refrigeration unit or industrial process refrigeration equipment containing 50 pounds or more of refrigerant, Fort Rucker personnel will make repairs if the appliance is leaking at a rate such that the loss of refrigerant will exceed 35% of the total charge during a 12-month period. Repairs will be made to reduce the leak rate to less than 35%. The current leak rate at time of discovery shall be pro-rated out to a 12-month period to determine if the 35% threshold is exceeded. Fort Rucker personnel will make necessary repairs to any commercial refrigeration unit or industrial process refrigeration equipment exceeding the 35% leak rate within 30 days. If additional time is required due to part availability, DPW ENRD will request an extension of up to 120 days from the EPA.

Following any repairs to leaking refrigeration appliances or equipment, Fort Rucker personnel shall perform a verification test within 30 days of bringing the unit/appliance back on-line to confirm the repairs have reduced the leak rate to less than the 35% rate. The verification test will be conducted at normal operating conditions (pressure and temperature) and characteristics.

14) Fort Rucker personnel shall repair leaks in any appliance that is not a commercial refrigeration unit or industrial process refrigeration equipment, which normally contains greater than 50pounds of refrigerant if the leak rate is greater than 15% of the total charge during a 12-month period. Repairs to such equipment must reduce the leak rate to less than 15% of the charge over a 12-month period. The current leak rate at time of discovery shall be pro-rated out to a 12-month period to determine if the 15% threshold is exceeded.

15) For any unit exceeding the 35% and 15% leak rate outlined above that Fort Rucker personnel  chooses not to repair, a one-year retrofit or replacement plan will be prepared within 30 days of discovery of leak rates in excess of threshold. Fort Rucker personnel will maintain this plan on file with DPW ENRD. The retirement plan will be dated and all work will be completed within one year of the date.

16) Container Sign-Out/In Procedures

a. Check oxygen level of refrigeration storage room. Oxygen level meter shall be on the 
    inside wall of the room. If level is low (oxygen deficient) OR level is high (oxygen 
 enriched), DO NOT ENTER - NOTIFY SUPERVISOR

b. If oxygen level is at normal range 19 to 21, the room may be entered.

c. Select correct refrigerant container for refrigerant to be recovered and service to be

             performed.

d. ALWAYS weigh Sign-Out or Sign-In container and record weight and other pertinent

             information on proper refrigerant management form.

e. To Sign-Out equipment, inspect equipment to be signed out to determine condition. If   

    not in usable condition, tag equipment as such and notify the ODC Compliance  

    Manager. If equipment is usable, equipment should be entered on the sign-out sheet to 
    include your name date and location to be used. To sign-in, reverse above procedure.

17) Disposing Refrigerant Appliances, Equipment, Oils, and Parts

        a. Using EPA certified recycling and recovery unit Fort Rucker personnel will attach proper  

            recovery equipment to containers making sure that all connections are tight, and then  

            remove refrigerant from appliance to the evacuation levels as listed in Table 1 of Section 
            III, transferring refrigerant to a DOT certified cylinder. All Class I and II ODC should be 
            turned in to The Defense Depot Richmond Virginia (DDRV) per the instruction located 
            in Attachment B.

b. Record amount of refrigerant recovered on appropriate forms and turn in to ODC    

    Compliance Manager at the end of day for recordkeeping.

c. Recover or drain oil in the system and deposit it in a certified oil containment vessel or

            drum.

d. When recovery is complete, remove recovery equipment and render the empty container

             unusable by puncturing or cutting it in half, per applicable safety standards, and label 
             appliance to be disposed of with appropriate label providing information as follows:

[image: image2.emf]
e. Place container in proper waste stream per DPW ENRD guidance. 

18) Technical procedures for Leak Testing Appliances

A) High or Very High Pressure Appliances:

1. Visual inspection of entire system.

a. oil trace 
a. broken lines or fittings

b. liquid indicator/moisture sight glass 
c. heavy frost or ice on components

d. temperature readings or indications

e. general run conditions

2. Audible 
a. listen for leaks 
b. listen for abnormal run conditions

3. Touch

a. check temperature of lines 
b. feel for oil on valves or refrigerant lines

4. Leak test 
a. halide torch

b. soap bubbles

c. electronic

d. audible

e. visual

f. dye

                            If a leak is determined to be present:

1. Install charging manifold on refrigerant system. (Install on both   

      high and low side of system, if possible.)

2. Isolate portion of system where leak is determined, if possible.  

If not possible, recover refrigerant from entire system into  DOT certified cylinder to evacuation levels specified in Table 1 in Section III.

3.   Repair leak per refrigerant safe practices.

3. Re-charge the system with trace R-22 and nitrogen to 5 – 30  

lbs. and leak test the entire system. If no leaks are found, pressurize to, at, or above refrigerant pressure for refrigerant used; e.g. 90 lbs. to 130 lbs. for R-12. If no leaks are found, move to triple vacuum procedure in accordance with evacuation levels specified in Table 1 in Section III, using micron gauge on third evacuation. If repair is not effective, repeat Step 3. If repair is effective, re-charge to proper operation conditions. Document all required refrigerant management forms and turn in to supervisor by the end of the work day.

B) Low Pressure Appliances:

                 Follow appliance manufacturer’s written operations and maintenance procedures.

19) Procedure for Rapid Response to Venting/Leaking of Refrigerant

A) Receive call from any Fort Rucker Facility during normal working

                 hours. PRIORITY ONE.

B) Respond to location of reported leak.

C) PERFORM A LIFE SAFETY CHECK! If life safety is an issue, call 911.

D) SECURE AREA! Allow no one to enter area or building. Wait for the proper

    authorities to arrive. Turn scene over to proper authorities.

E) If life safety is not an issue, determine source of leak. Shut down system. Isolate leak   

     if possible.

F) Recover refrigerant following proper procedures and evacuation levels.

G) Determine repair necessary.

H) Repair appliance and conduct leak test.

20) Safe Handling of Refrigerants

CAUTION

Liquid refrigerant can cause frostbite if skin contact occurs. Be aware that the refrigerant/oil being removed from a system may contain contaminants which may be harmful to breathe or contact with the skin. Always provide fresh, clean air when working in enclosed areas. Avoid breathing vapors. Always wear safety glasses and gloves (cold resistant for pressurized refrigerant and rubber for F-11 and R-113). Avoid contact with clothing.

· Only fill containers which are currently DOT approved for fluorocarbon refrigerants.

· Always inspect the container for pressure rating and latest hydrostatic test date.

· Be sure to thoroughly check each container for dents, gouges, bulges, cuts, or any other imperfections which may render it unsafe to hold refrigerant for storage or transportation.

· Do not fill a container which does not have a current hydrostatic date. Do not risk filling a container which appears unsafe or may leak.

· Always use a scale when filling any container. Do not overfill.

· Make sure all connections are made tight before transferring refrigerants into containers.

· Also, make sure all closures are made tight on the container immediately after filling.

· Document all required EPA refrigerant management information on proper refrigerant management forms and turn in to ODC Compliance Manager by the end of the workday.
Section V. Recycling and Recovery Equipment

Fort Rucker personnel will comply with EPA’s certification program for refrigerant recovery and recycling equipment. Under this program, EPA requires that manufacturers or importers of refrigerant recovery and recycling equipment manufactured on or after November 15, 1993, have their equipment tested by an EPA-approved testing organization to ensure that it meets EPA requirements. 
· All Fort Rucker personnel equipment intended for use with air-conditioning and refrigeration appliances shall be tested under EPA requirements based upon the ARI 740 test protocol (i.e., EPA Appendices B and B1 to 40 CFR 82 subpart F). 
· All Fort Rucker personnel recycling and recovery equipment used with small appliances shall be tested under EPA Appendix C or alternatively under requirements based upon the ARI 740 test protocol (i.e., Appendices B and B1 to 40 CFR 82 subpart F).

· All Fort Rucker personnel shall provide a yearly current inventory of certified recycling and recovery equipment in use to the Environmental Natural Resource Division Air Quality Manager. 
· All outside personnel engaged in any HVAC work that requires evacuation of refrigerant are required to sign a Contractor Agreement form (Attachment C) acknowledging compliance with the Fort Rucker Refrigerant Management Program and verifying that all recycling and recovery equipment used for equipment on Fort Rucker has been certified.
The recovery efficiency standards required by EPA vary depending on the size and type of air conditioning or refrigeration equipment being serviced. For recovery and recycling equipment intended for use with air-conditioning and refrigeration equipment besides small appliances, these standards are the same as those in the second column of Table 1 in Section III of this RMP. Recovery equipment intended for use with small appliances must be able to recover 90 percent of the refrigerant in the small appliance when the small appliance compressor is operating and 80 percent of the refrigerant in the small appliance when the compressor is not operating.

Section VI. Technician Certification/Training

Any Fort Rucker personnel that performs repair, maintenance, service, or disposal to any appliance that could reasonably be expected to have the potential to release refrigerants to the ambient air must be an EPA approved certified technician prior to conducting such work. For the purpose of Fort Rucker refrigerant management program, a technician is someone who:

· Attaches and detaches hoses and/or gauges to an appliance for the purpose of measuring internal pressure of the appliance;

· Adds or removes refrigerant from an appliance;

· Conducts any other activity that may compromise the integrity of the small appliance and MVAC-like appliances.
HVAC apprentice technicians are exempt from these certification requirements provided the

apprentice is supervised at all times by a certified technician whenever maintaining, servicing,

repairing, or disposing an appliance.
Type I - for servicing small appliances;

Type II - for servicing or disposing of high-pressure or very high-pressure appliances,

except small appliances and MVACs;

Type III - for servicing or disposing of low-pressure appliances;

Universal - for servicing all types of equipment.
All Fort Rucker personnel shall provide a yearly inventory of technicians who have taken and passed an EPA-approved test administered by an EPA-approved certifying organization, the results of which are maintained on file at the Environmental Natural Resource Division.

Section VII. Recordkeeping

1)  All Fort Rucker personnel will complete field sheets and maintain records indicating the amount of refrigerant that has been added to all appliances (including units with less than 50 pounds of refrigerant). The ODC Compliance Manager will maintain copies of all field sheets for at least six years.

2)  For a period of at least 6 years, Fort Rucker personnel will maintain and possess the following records on-site for units containing more that 50 lbs. of Class I or Class II refrigerant:

· Leak rate,

· Method used to determine the leak rate and full charge,

· Date a leak rate of greater than the allowable annual leak rate was discovered,

· The location of leak (s) to the extent determined to date,

· Any repair work that has been completed thus far and the date that work was

· completed, and

· Dates and types of all initial and follow-up verification tests performed and the test

results for all initial and follow-up verification tests must be maintained and

submitted to EPA within 30 days after conducting each test where record keeping

and reporting is required. 

3) The ODC Compliance Manager will track appliance information including refrigerant usage, 
     leaks, disposal, and service records.

4) Fort Rucker personnel shall maintain records of all refrigerant purchases, including type, 
    amount, date, and supplier information. 

5) Copies of the EPA certification for each recycling and recovery unit will be maintained on 
    file.

ATTACHMENT A: Refrigeration Field Sheet

[image: image3.emf]
ATTACHMENT B: General ODC Turn-in Procedure

[image: image4.emf]
[image: image5.emf]
[image: image6.emf]

[image: image7]
ATTACHMENT C: Contractor/Subcontractor Agreement

I, _______________________________, do hereby acknowledge that all of our service technicians have received training on venting, recovery, recycling, and replacement of chlorofluorocarbons (CFCs), hydrochlorofluorocarbons (HCFCs), and other refrigerants used in air conditioning and refrigerant systems, units, and small appliances, and have taken and passed an EPA-approved test appropriate for the equipment that they service and/or dispose of. I agree that all of our service technicians will follow procedures for servicing, repairing, and disposing of any and all refrigerant-containing devices, units, and systems as outlined by Fort Rucker policy and federal, state, and local laws and regulations now in effect or hereinafter enacted which pertain to the Federal Clean Air Act of 1990. I am aware of the significant harm to the earth’s atmosphere caused by venting refrigerants into the air. We agree not to willfully vent refrigerants into the air under any circumstances. I understand that our organization will be held responsible and liable if I or any of our service technicians willfully violate the Federal Clean Air Act of 1990 regarding venting of refrigerants and that we are liable for any and all fines associated with violations (currently up to $32,500 per occurrence). Any unintentional venting will be documented in accordance with company policy. I understand that if we willfully violate the Clean Air Act of 1990, we will fully protect, indemnify, hold harmless, and defend the United States Army Aviation Center of Excellence and Fort Rucker from and against any and all liability regarding the handling, venting, and/or disposal of any and all refrigerants.

We also agree to provide a copy of the Federal Certification numbers for all our service technicians. Should any certifications be revoked, we will notify the United States Army Aviation Center of Excellence and Fort Rucker immediately. 

Signed ______________________________________ Date _______________________

Printed Name ________________________________________________________________________

Company Name ________________________________________________________________________ 

Technician Name _______________________________ 

Certification No.________________

Page 1 of 20
This is a controlled document.

Please verify the latest version online.
Page 20 of 20
This is a controlled document.

Please verify the latest version online.


[image: image1.emf]